WATER SAFETY Legionella Control Log Book Monitoring and maintenance record for hot and cold water systems [Organisation name] [Site or building]

Important: please read before use This template is provided by Trefnus for general guidance only. It does not constitute professional, legal or health and safety advice, and it is not a substitute for a competent Legionella risk assessment or a site-specific written scheme of control. Trefnus accepts no liability for any loss or damage arising from the use of this template. Responsibility for the accuracy, completeness, suitability and legal compliance of any completed document rests solely with the user. You should obtain advice from a competent person where appropriate. By using this template you accept these terms.

About this log book

This log book records the routine monitoring, inspection and maintenance carried out to control the risk of Legionella bacteria in the water systems at this site. Kept up to date, it provides documented evidence of the monitoring and maintenance activities undertaken as part of the written scheme of control.

It supports the duty holder in meeting their responsibilities under the Health and Safety at Work etc. Act 1974, the Control of Substances Hazardous to Health Regulations 2002 (COSHH), and the HSE Approved Code of Practice L8 with the supporting technical guidance HSG274.

How to use this log book

- Record every task on the correct log as soon as it is completed. Enter the date, the reading or result, and your initials.

- Follow the monitoring frequencies set out in your site risk assessment and written scheme. The frequencies noted here are typical starting points, not a substitute for your own assessment.

- Where a reading falls outside the required standard, or a task cannot be completed, record it on the Remedial and corrective actions log and notify the responsible person.

- Keep this log book, the risk assessment and the written scheme of control together and available for inspection.

- Duplicate any log page as required.

- Retention: keep monitoring, inspection and test records for at least five years. Keep the risk assessment and written scheme of control while they remain current and for at least two years after they are superseded.

Site and document details

| Organisation | [Organisation name] | Site / building | [Site or building] |
| --- | --- | --- | --- |
| Site address | [Address and postcode] |  |  |
| Log book reference | [Reference] | Version | [Version / date] |
| Period covered: from | [Date] | to | [Date] |
| Date opened | [Date] | Responsible person | [Name] |
| Document owner | [Name] | Controlled copy status | [Controlled / uncontrolled] |

Amendment history

Record changes to this log book so that the current version and its history are clear.

| Version | Date | Summary of change | Author |
| --- | --- | --- | --- |

Responsible persons

Record the people who hold each role for this site. The duty holder (the employer or organisation in control of the premises) has overall responsibility for controlling the risk; the responsible person manages the scheme day to day.

| Role | Name | Organisation | Contact (phone / email) |
| --- | --- | --- | --- |
| Duty holder |  |  |  |
| Responsible person |  |  |  |
| Deputy responsible person |  |  |  |
| Water treatment / service contractor |  |  |  |
| Independent consultant (if appointed) |  |  |  |
| Out-of-hours / emergency contact |  |  |  |

Contractor and competency details

Where tasks are carried out by contractors, record their competency evidence. Water treatment and monitoring contractors are commonly members of the Legionella Control Association (LCA); laboratories should be UKAS-accredited.

| Contractor / organisation | Service provided | Accreditation (e.g. LCA) | Insurance expiry / notes |
| --- | --- | --- | --- |

Reporting a problem If you identify a fault, an out-of-range reading, discoloured or unusual water, or a suspected case of illness linked to the water system, stop and notify the responsible person without delay and record it on the Remedial and corrective actions log.

Water system asset register

List the main components of the water system covered by this log book. This gives everyone a shared reference when recording checks and reporting faults.

| Ref | Description / type | Location | Material / notes |
| --- | --- | --- | --- |

Risk assessment record

This log book supports, but does not replace, the site Legionella risk assessment and the written scheme of control. Record the current assessment below and keep the full documents with this log book.

| Risk assessment reference | [Reference] |
| --- | --- |
| Assessed by | [Name / organisation] |
| Date completed | [Date] |
| Next review due | [Date] |
| Written scheme location | [Where the control scheme is held] |
| System schematic available / location | [Yes / No, where held, date last reviewed] |
| Key higher-risk assets |  |

Review the risk assessment when it may no longer be valid Including: the system is altered; building use or occupancy changes; a positive Legionella sample or an associated case of illness; significant or repeated temperature failures; a change of responsible person; or at the review interval set by the assessment.

System operational status

L8 expects the records to show the state of operation of the system. Record here any outlet or part of the system taken out of use, capped or removed, and any return to use, so that flushing, capping or removal is managed and evidenced. Statuses: in use, out of use, capped, removed, returned to use.

| Asset / outlet | Location | Status | Date changed | Action taken | By |
| --- | --- | --- | --- | --- | --- |

Temperature standards to apply Hot water: stored at 60°C or above; where a secondary return is fitted, returning at 50°C or above (55°C in healthcare premises); reaching 50°C at sentinel outlets within one minute of running (55°C in healthcare premises). Cold water: below 20°C at sentinel outlets within two minutes of running. Danger zone: Legionella multiplies between 20°C and 45°C. Keep hot water hot and cold water cold. Out-of-range readings: investigate the cause and record the finding and any action on the Remedial and corrective actions log.

How this log book supports L8 L8 expects the duty holder to assess the risk, appoint a competent responsible person, prepare a written scheme of control, implement and monitor the measures, keep records, and review the assessment. This log book provides the record of monitoring, inspection, maintenance and remedial action. It supports the written scheme; it does not replace the risk assessment or the scheme. The records L8 expects include: the names and posts of those responsible; the significant findings of the risk assessment; the written scheme and how it is implemented; the state of operation of the system; and the results of monitoring, inspections, tests and checks, with dates.

Monitoring outlet register

List the outlets used for monitoring and give each a unique ID (for example HW-01, CW-01). Identify the sentinel outlets (nearest and furthest on each system) and any representative outlets. Use these IDs on the temperature and flushing sheets so that readings can be compared over time.

| Outlet ID | Description / location | System (HW/CW) | Monitoring role | Asset ref |
| --- | --- | --- | --- | --- |

Thermometer and probe calibration

Temperature monitoring is only reliable if the instruments are calibrated. Record the calibration of each thermometer or probe and keep the certificates with this log book. Auditors commonly ask for these records.

| Instrument / probe ID | Serial number | Calibration date | Certificate reference | Next due | Verified by |
| --- | --- | --- | --- | --- | --- |

1.  Monthly temperature monitoring

Frequency: monthly at sentinel outlets (nearest and furthest on each system), plus a rotating selection of representative outlets to give reasonable confidence that the whole system remains under control. Hot ≥ 50°C within one minute; cold < 20°C within two minutes. Record any failure on the Remedial and corrective actions log.

Written scheme reference: ______________________	Sheet ______ of ______

| Date | Outlet reference / location | HOT WATER |  | COLD WATER |  | Satisfactory (Y/N) | Initials |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Temp °C | ≤ 1 min? (Y/N) | Temp °C | ≤ 2 min? (Y/N) |  |  |

Duplicate this page as required. One row per outlet, per check.

2.  Calorifier and hot water heater temperatures

Frequency: monthly. Stored hot water should modulate as close to 60°C as practicable without falling below it. Where a secondary return circulation is fitted, the return should be 50°C or above (55°C in healthcare premises). Record the annual internal inspection and drain-down on the Annual and periodic tasks register (log 7).

Written scheme reference: ______________________	Sheet ______ of ______

| Date | Unit reference / location | Stored / flow temp °C (≥ 60) | Return temp °C (≥ 50, if fitted) | Satisfactory (Y/N) | Comments / action reference | Checked by |
| --- | --- | --- | --- | --- | --- | --- |

3.  Cold water storage tank inspection

Frequency: inspect and carry out any remedial work normally annually, or as the risk assessment requires. Check the stored water temperature (remote from the ball valve) and the incoming mains temperature at least annually (summer) or as temperature profiling indicates. Stored cold water should be below 20°C. Check the lid, insect screens, insulation and internal condition for debris, corrosion or contamination.

Written scheme reference: ______________________	Sheet ______ of ______

| Date | Tank reference / location | Stored temp °C (< 20) | Incoming mains temp °C | Lid, screens & insulation OK (Y/N) | Internal condition satisfactory (Y/N) | Inspector |
| --- | --- | --- | --- | --- | --- | --- |

4.  Little-used outlet flushing

Frequency: weekly (or as the risk assessment requires). In accordance with the written scheme, flush each infrequently used outlet until the temperature stabilises and is comparable to the supply water, then purge to drain. Enter the week ending date at the top of each column and initial each cell when the outlet has been flushed.

Written scheme reference: ______________________	Sheet ______ of ______

| Outlet reference / location | Week ending __ / __ | Week ending __ / __ | Week ending __ / __ | Week ending __ / __ | Week ending __ / __ | Week ending __ / __ | Week ending __ / __ | Week ending __ / __ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

5.  Showerhead and spray outlet cleaning

Frequency: quarterly (or as the risk assessment requires). Dismantle, clean, descale and disinfect showerheads, hoses and spray taps, which generate aerosols and are therefore an important control point.

Written scheme reference: ______________________	Sheet ______ of ______

| Date | Outlet reference / location | Task (clean / descale / disinfect) | Satisfactory (Y/N) | Next due | Initials | Comments |
| --- | --- | --- | --- | --- | --- | --- |

6.  Thermostatic mixing valve (TMV) service

Frequency: risk based, commonly six-monthly to annually. Inspect, clean, descale and disinfect; confirm the fail-safe shut-off operates when the cold supply is isolated; and verify the blended outlet temperature is within the safe range set by the written scheme.

Written scheme reference: ______________________	Sheet ______ of ______

| Date | TMV reference / location | Clean, descale, disinfect (Y/N) | Fail-safe operates (Y/N) | Blended temp °C | Satisfactory (Y/N) | Next due | Serviced by |
| --- | --- | --- | --- | --- | --- | --- | --- |

7.  Annual and periodic tasks

Record the less-frequent inspection, maintenance and disinfection tasks here. Frequencies are the typical HSG274 Part 2 starting points; apply the frequency set by your risk assessment.

| Task | Typical frequency | Asset / location | Date completed | Next due | Completed by |
| --- | --- | --- | --- | --- | --- |
| Calorifier internal inspection and drain, debris and clarity check | Annually |  |  |  |  |
| Cold water storage tank clean and disinfect (as required) | Annually / as needed |  |  |  |  |
| Tank, pipework and fittings insulation check | Annually |  |  |  |  |
| Thermostatic mixing valve service and fail-safe test | 6-monthly to annually |  |  |  |  |
| Point-of-use / small water heater temperature check | Monthly to 6-monthly |  |  |  |  |
| Base-exchange water softener service and disinfection | Annually |  |  |  |  |
| Expansion vessel flush / throughflow check | Per risk assessment |  |  |  |  |
| System disinfection after works or an adverse result | As required |  |  |  |  |

8.  Disinfection, commissioning and system changes

Record significant one-off events here: thermal or chemical disinfection, pasteurisation after a failure, commissioning of new plant, and system modifications such as new outlets, refurbishments or the removal of dead legs. Keep any disinfection or commissioning certificates with this log book. Examples of activity: thermal disinfection, chemical disinfection, commissioning, system modification, dead-leg removal.

| Date | Activity | System / location | Reason | Result / certificate reference | Completed by |
| --- | --- | --- | --- | --- | --- |

9.  Legionella monitoring and sampling results

Routine Legionella sampling is not required for most simple systems where temperature control is effective. Record any sampling carried out here, for example where the risk assessment requires it, in higher-risk or healthcare premises, or to confirm remediation after an adverse result. Use a UKAS-accredited laboratory and keep the certificates of analysis with this log book.

| Date sampled | Sample point / outlet | Reason for sample | Laboratory | Result (CFU/L) | Action level exceeded? (Y/N) | Action taken / reference |
| --- | --- | --- | --- | --- | --- | --- |

10.  Monthly compliance summary

A month-by-month overview for management. Summarise the checks due and completed, any missed or out-of-range results, and the corrective actions raised, closed and outstanding. Use the comments column to note seasonal changes or repeat failures so that deteriorating performance is spotted early.

| Month | Checks due | Completed | Missed | Out of range | Actions raised | Actions closed | Outstanding | Comments / seasonal note | Reviewed by |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

11.  Remedial and corrective actions

Record every out-of-range reading, missed task, fault, adverse sample or concern here. Give each a reference and priority, note the root cause and the action taken (including any disinfection), and sign off when verified. This is the record that shows problems were fully resolved.

| Ref | Date raised | Priority | Location / system | Issue and root cause | Action taken | Owner | Target date | Date verified | Verified by (sign) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Training record

Everyone carrying out tasks in this log book should be competent to do so. Record training, briefings and refreshers here.

| Name | Role | Training / briefing | Provider | Date | Refresher due |
| --- | --- | --- | --- | --- | --- |

Review and audit log

Use this log to record risk assessment reviews, scheme audits and periodic checks that the control measures remain effective.

| Date | Review type | Reviewed by | Outcome / actions | Next review due |
| --- | --- | --- | --- | --- |

Sign-off

By signing below, the responsible person and duty holder confirm that this log book has been reviewed and is being used to record the monitoring and maintenance activities for the site water systems.

| Role | Name | Signature | Date |
| --- | --- | --- | --- |
| Responsible person |  |  |  |
| Duty holder |  |  |  |

| Issue date |  | Next review date |  |
| --- | --- | --- | --- |

Appendix: reference

For quick reference. This log book should be read alongside the site risk assessment, the written scheme of control, and HSG274 Part 2. Always defer to your site risk assessment and written scheme where they specify different values or frequencies.

A1   Temperature standards

| Point | Standard |
| --- | --- |
| Calorifier flow (hot water storage) | 60°C or above |
| Hot water return | 50°C or above (55°C healthcare) |
| Hot water at sentinel outlets | 50°C within 1 min (55°C healthcare) |
| Cold water at sentinel outlets | Below 20°C within 2 min |
| Legionella danger zone | 20°C to 45°C |

A2   Recommended monitoring frequencies

| Task | Typical frequency |
| --- | --- |
| Hot and cold sentinel outlet temperatures | Monthly |
| Calorifier flow and return temperatures | Monthly |
| Calorifier internal inspection and drain / debris check | Annually |
| Cold water storage tank inspection | Annually |
| Stored and incoming mains water temperature | Annually (summer), or per profiling |
| Representative outlet temperatures (system profile) | Rotational, over a defined period |
| Little-used outlet flushing | Weekly |
| Showerhead, hose and spray outlet cleaning and descaling | Quarterly |
| Thermostatic mixing valve service and fail-safe check | 6-monthly to annually (risk based) |
| Point-of-use / small water heater temperature | Monthly to 6-monthly |
| Base-exchange water softener service | Annually |
| Risk assessment review | When no longer valid (e.g. system, use, occupancy or result changes) |

A3   Record keeping and retention (L8)

For sites with five or more employees, L8 expects the records to include:

- The names and posts of the people responsible for the risk assessment, and for managing and implementing the scheme.

- The significant findings of the risk assessment.

- The written scheme of control and details of how it is implemented.

- The state of operation of the system (in use or out of use).

- The results of any monitoring, inspection, test or check, and the dates.

Retention: keep monitoring, inspection and test records for at least five years. Keep the risk assessment and written scheme while they remain current and for at least two years after they are superseded.

A4   Roles and key terms

- Duty holder: the employer or person in control of the premises, with legal responsibility for controlling the risk.

- Responsible person: the competent, appointed person who manages the control scheme day to day.

- Sentinel outlets: the outlets nearest to and furthest from each hot and cold water source, used as representative monitoring points.

- Little-used outlet: any outlet used infrequently, commonly taken as not used within a week.

- Written scheme of control: the site-specific document describing the system, the risks, and the measures used to control them.

A5   Guidance and legislation

- HSE ACOP and guidance L8: Legionnaires’ disease. The control of legionella bacteria in water systems.

- HSG274 Part 1 (evaporative cooling systems), Part 2 (hot and cold water systems), Part 3 (other risk systems).

- Health and Safety at Work etc. Act 1974; COSHH 2002; Management of Health and Safety at Work Regulations 1999.